### Unofficial Solis Communication protocol
#### 1. Overview
This protocol adopted MODBUS RTU regulation, is applicable to the communication
protocol between SOLIS grid-tied inverter and PC monitoring software. This protocol can
read operational information and control the inverter in real time.

#### 2. Physical interface
#### 2.1 Adopts RS485 Receiver-Transmitter, Client-Server Model
----Baud rate：9600bps
----Parity checking：None
---- Data：8
---- Stop：1
#### 2.2 Inter-frame interval requirement:
More than 300ms communications frame interval is required. Recommended max data frame
100 bytes (50 registers)

#### 3. Detail description of the Protocol
00001-09999(0X) register address is writable register type, support 0x05 function code ，
10001-19999(1X) register address is read-only register type，support 0x02 function code，
30001-39999 (3X) register address is a read-only register type, support 0x04 functioncode,
40001-49999 (4X) register address is a readable and writable holding register
      address, and support 0x03, 0x06, 0x10 function code

Note: In practice, however, the register address 0001-9999 is used in these function codes.

#### 4. Register address of inverter operation information.
The function code is 0x04, the register address needs to offset one bit.
Example: While the Battery SOC is at 33139 (0-based) a direct poll (e.g. with mbpoll command) needs to request the register number 33140 (1-based).
ALL TABLES BELOW ARE 0-BASED

Table 1 – Environment Registers (0-based)
Register	Name	Data Type	Unit	Remark
33093	Wechselrichter Temperatur	S16	0.1°C
33096	Batterie Temperatur	S16	0.1°C	NOT SURE ABOUT IT

Table 2 – Battery Registers (0-based)
Register	Name	Data Type	Unit	Remark
33133	Batterie Spannung	U16	0.1V
33134	Batterie Stromstärke	U16	0.1A
33135	Batterie Status	U16		0 = charge | 1 = discharge
33139	Batterie SOC	U16	%
33140	Batterie SOH	U16	%
33149	Batterie aktuelle Leistung	S32	1W	Direction not confirmed
33161	Batterie gesamt geladen	U32	1kWh
33163	Batterie heute geladen	U16	0.1kWh
33165	Batterie gesamt entladen	U32	1kWh
33167	Batterie heute entladen	U16	0.1kWh

Table 3 – Grid Registers (0-based)
Register	Name	Data Type	Unit	Remark
33147	Hausverbrauch	U16	1W
33151	WR Netzbezug/Einspeisung (aktuell)	S32	1W	„+ val“ to grid | „- val“ from grid / (Direction not confirmed)
33169	WR Netzbezug (gesamt)	U32	1kWh
33171	WR Netzbezug (heute)	U16	0.1kWh
33173	WR Einspeisung (gesamt)	U32	1kWh
33175	WR Einspeisung (heute)	U16	0.1kWh
33177	Hausverbrauch (gesamt)	U32	1kWh
33179	Hausverbrauch (heute)	U16	0.1kWh

Table 4 – PV Registers (0-based)
Register	Name	Data Type	Unit	Remark
33029	PV Leistung (gesamt)	U32	1kWh
33031	PV Leistung (Monat)	U32	1kWh
33035	PV Leistung (heute)	U16	0.1kWh
33037	PV Leistung (Jahr)	U32	1kWh
33049	String 1 Spannung	U16	0.1V
33050	String 1 Stromstärke	U16	0.1A
33051	String 2 Spannung	U16	0.1V
33052	String 2 Stromstärke	U16	0.1A
33053	String 3 Spannung	U16	0.1V
33054	String 3 Stromstärke	U16	0.1A
33055	String 4 Spannung	U16	0.1V
33056	String 4 Stromstärke	U16	0.1A
33057	PV Leistung (DC)	U32	1W
33079	PV Leistung (AC)	S32	1W