### Solis Communication protocol
#### 1. Overview
This protocol adopted MODBUS RTU regulation, is applicable to the communication
protocol between SOLIS grid-tied inverter and PC monitoring software. This protocol can
read operational information and control the inverter in real time.

#### 2. Physical interface
#### 2.1 Adopts RS485 Receiver-Transmitter, Client-Server Model
----Baud rate：9600bps
----Parity checking：None
---- Data：8
---- Stop：1
#### 2.2 Inter-frame interval requirement:
More than 300ms communications frame interval is required. Recommended max data frame
100 bytes (50 registers)

#### 3. Detail description of the Protocol
00001-09999(0X) register address is writable register type, support 0x05 function code ，
10001-19999(1X) register address is read-only register type，support 0x02 function code，
30001-39999 (3X) register address is a read-only register type, support 0x04 functioncode,
40001-49999 (4X) register address is a readable and writable holding register
      address, and support 0x03, 0x06, 0x10 function code

Note: In practice, however, the register address 0001-9999 is used in these function codes.

#### 4. Register address of inverter operation information.
The function code is 0x04, the register address needs to offset one bit.
Example: register address: 3000, the send address is 2999.

Register	Name	Data Type	Unit	Remark	Address / type

3005-3006	Active Power	U32	1W		3x
3042	Inverter Temp	U16	0,1 °C		3x

3022	DC 1 Voltage	U16	0,1V		3x
3023	DC 1 Current	U16	0,1A		3x
3024	DC 2 Voltage	U16	0,1V		3x
3025	DC 2 Current	U16	0,1A		3x
3026	DC 3 Voltage	U16	0,1V		3x
3027	DC 3 Current	U16	0,1A		3x
3028	DC 4 Voltage	U16	0,1V		3x
3029	DC 4 Current	U16	0,1A		3x
3007-3008	Total DC Output	U32	1W		3x

3009-3010	Total Energy	U32	1kWh		3x
3011-3012	Energy Month	U32	1kWh		3x
3015	Energy Day	U16	0,1 kWh		3x
3017-3018	Energy Year	U32	1kWh	Min 15k	3x
3080-3081	Meter Total active generation	U32	1Wh	1 <=> 1Wh	3x
3084-3085	Meter Active Power	U32	1W	+ to grid / - from grid	3x

3283-3284	Meter Grid Import Energy	U32	0,01kWh	100 <=> 1kWh	3x
3285-3286	Meter Grid Export Energy	U32	0,01kWh	100 <=> 1kWh	3x